## 1 - Goal and scope definition
TEA of a conventional underground power cable between Al Dhafra PV power plant and Dubai airport
Phase 1: Goal and scope definition
Goal | Product system | Aluminum power cable system
| Intended application and reasons for study | Comparison with HTS cable system
| Brief description | Transmission link between solar plant and substation
| Intended audience | Tutorial HTS school COST ACTION Hi-scale
| Comissioners and assessors | L. Quéval & A. Musso
| Limitations of study | Do not trust the data !
Scope | System boundary | Cable system including transformer
| Benchmark system | 400 kV underground cable
| Plant size | 2 GW
| Functional unit | 750 MW
| System elements and technology maturity | TRL 9
| Performance indicators | Life cycle cost (LCC)
| Time horizon | 40 years
| Location | Saudi Arabia
| Operation continuity | 8 hours a day

## 2 - Inventory analysis
TEA of a conventional underground power cable between Al Dhafra PV power plant and Dubai airport
Phase 2: Inventory analysis
System
Technical parameter | Symbol | Value | Units | Comment
cable length | Ln | 32000 | [m]
nominal power | Pn | 1500000000 | [W]
nominal voltage | Un | 400000 | [V L-L RMS]
nominal power factor | PFn | 0.95 | [-]
frequency | f | 50 | [Hz]
Economic parameter | Symbol | Value | Units | Comment
cost of electricity | Celec | 1.5e-05 | [€/Wh] | 15€/MWh
nb of operating hours year | nhpy | 2920 | [-] | 8760 hours in a year, considering 8 hours per day
system lifetime | L | 40 | [years]
discount rate | dr | 0.05 | [-]
Cable
Technical parameter | Symbol | Value | Units | Comment
nominal voltage | Vn_cab | 220000 | [kV L-N RMS]
ampacity | In_cab | 1800 | [A/core]
AC resistance per m @90degC | r_cab | 1.36e-05 | [Ohm/m]
inductance per m | l_cab | 6.4e-07 | [H/m]
capacitance per m | c_cab | 2.3e-10 | [F/m]
Factor of loss of insulation | tand_cab | 0.001 | [-]
Economic parameter | Symbol | Value | Units | Comment
cable cost per km per core | C_cab | 937.5 | [€/m/core] | including trench, laying, routing, fittings, tests, etc.
Transformer
Technical parameter | Symbol | Value | Units | Comment
nominal apparent power | Sn_transfo | 800000000 | [VA]
efficiency | eta_transfo | 0.996 | [-]
Economic parameter | Symbol | Value | Units | Comment
Unit cost of a 800 MVA transfo | UC_transfo | 4733000 | [€]
Land
Technical parameter | Symbol | Value | Units | Comment
Economic parameter | Symbol | Value | Units | Comment
cost of land | C_land | 36 | [€/m] | 20€/m2 *1.8m of right of way per 1x 3ph circuit

## 3 - Calculation of indicators
TEA of a conventional underground power cable between Al Dhafra PV power plant and Dubai airport
Phase 3: Calculation of indicators
Cable | [5 empty] | Cost | Discounted Cost
Technical model | Symbol | Value | Units | Comment | Year | Value | Value | Units | Comment
Circuit nominal current | In | 2279.0142 | [A] | In = Pn/(sqrt(3)*Un*PFn) | 1 | 202196610.8436 | 192568200.8035 | € | CAPEX+OPEX
Nb of circuits | Ncir | 2 | [-] | Ncir = ceil(In/In_cab) | 2 | 960610.8436 | 871302.3525 | € | OPEX
Nb of cables | N_cab | 6 | [-] | N_cab = 3*Ncir | 3 | 960610.8436 | 829811.7643 | € | OPEX
Joule losses | Pj_cab | 8460288 | [W] | Pj_cab = N_cab*r_cab*Ln*In_cab^2 | 4 | 960610.8436 | 790296.9184 | € | OPEX
Dielectric losses | Pd_cab | 671466.4209 | [W] | Pd_cab = N_cab*2*pi*f*c_cab*Ln*Vn_cab^2*tand_cab | 5 | 960610.8436 | 752663.7318 | € | OPEX
annual energy losses | AElosses_cab | 26664722908.9095 | [Wh] | AElosses_cab = (Pj_cab+Pd_cab)*nhpy | 6 | 960610.8436 | 716822.6017 | € | OPEX
Economic model | Symbol | Value | Units | Comment | 7 | 960610.8436 | 682688.1921 | € | OPEX
investment cost | CAPEX_cab | 180000000 | [€] | CAPEX_cab = N_cab*C_cab*Ln | 8 | 960610.8436 | 650179.2306 | € | OPEX
annual cost of losses | OPEX_cab | 399970.8436 | [€/year] | OPEX_cab = Celec*AElosses_cab | 9 | 960610.8436 | 619218.3148 | € | OPEX
[5 empty] | 10 | 960610.8436 | 589731.7284 | € | OPEX
Transformer |  |  |  |  | 11 | 960610.8436 | 561649.2651 | € | OPEX
Technical model | Symbol | Value | Units | Comment | 12 | 960610.8436 | 534904.062 | € | OPEX
Nb of 3ph transfo | N_transfo | 4 | [-] | N_transfo = 2*ceil(Pn/PFn/Sn_transfo), 2x bc one transfo at each end of the line, account for 0% margin | 13 | 960610.8436 | 509432.44 | € | OPEX
power losses | Plosses_transfo | 12800000 | [W] | Plosses_transfo = N_transfo*(1-eta_transfo)*Sn_transfo | 14 | 960610.8436 | 485173.7524 | € | OPEX
annual energy losses | AElosses_transfo | 37376000000 | [Wh] | AElosses_transfo = Plosses_transfo*nhpy | 15 | 960610.8436 | 462070.2404 | € | OPEX
Economic model | Symbol | Value | Units | Comment | 16 | 960610.8436 | 440066.8956 | € | OPEX
investment cost of transfo | CAPEX_transfo | 18932000 | [€] | CAPEX_transfo = N_transfo*UC_transfo | 17 | 960610.8436 | 419111.3292 | € | OPEX
annual cost of losses | OPEX_transfo | 560640 | [€/year] | OPEX_transfo = Celec*AElosses_transfo | 18 | 960610.8436 | 399153.6468 | € | OPEX
[5 empty] | 19 | 960610.8436 | 380146.3303 | € | OPEX
Land |  |  |  |  | 20 | 960610.8436 | 362044.1241 | € | OPEX
Technical model | Symbol | Value | Units | Comment | 21 | 960610.8436 | 344803.9277 | € | OPEX
| - |  |  |  | 22 | 960610.8436 | 328384.6931 | € | OPEX
Economic model | Symbol | Value | Units | Comment | 23 | 960610.8436 | 312747.3267 | € | OPEX
investment cost | CAPEX_land | 2304000 | [€] | CAPEX_land = Ncir*C_land*Ln | 24 | 960610.8436 | 297854.5969 | € | OPEX
[5 empty] | 25 | 960610.8436 | 283671.0446 | € | OPEX
System |  |  |  |  | 26 | 960610.8436 | 270162.8997 | € | OPEX
Technical model | Symbol | Value | Units | Comment | 27 | 960610.8436 | 257297.9997 | € | OPEX
| - |  |  |  | 28 | 960610.8436 | 245045.714 | € | OPEX
Economic model | Symbol | Value | Units | Comment | 29 | 960610.8436 | 233376.8705 | € | OPEX
Capital expenditure (assumed at t=0) | CAPEX | 201236000 | [€] |  | 30 | 960610.8436 | 222263.6862 | € | OPEX
Yearly operational expenditure | OPEX_t | 960610.8436 | [€/year] |  | 31 | 960610.8436 | 211679.7011 | € | OPEX
Life cycle cost | LCC | 208136537.7518 | [€] | LCC= Sum((CAPEX_t+OPEX_t)/(1+r)^y) | 32 | 960610.8436 | 201599.7153 | € | OPEX
[5 empty] | 33 | 960610.8436 | 191999.7289 | € | OPEX
[5 empty] | 34 | 960610.8436 | 182856.8847 | € | OPEX
[5 empty] | 35 | 960610.8436 | 174149.414 | € | OPEX
[5 empty] | 36 | 960610.8436 | 165856.5847 | € | OPEX
[5 empty] | 37 | 960610.8436 | 157958.6521 | € | OPEX
[5 empty] | 38 | 960610.8436 | 150436.8115 | € | OPEX
[5 empty] | 39 | 960610.8436 | 143273.1538 | € | OPEX
[5 empty] | 40 | 960610.8436 | 136450.6227 | € | OPEX
[5 empty] | NVP 40 years |  | 208136537.7518 | €
[5 empty] | NVP 25 years |  | 205192129.313 | €
[5 empty] | NVP 10 years |  | 199070915.638 | €

## 4 - Interpretation
TEA of a conventional underground power cable between Al Dhafra PV power plant and Dubai airport
Phase 4: Interpretation
Sensitivity analysis
Variable | Symbol | Value | Units | Comment
Life cycle cost (T=40y, dr=0.05) | LCC 1 |  | € | 40 years and discount rate = 0.05
Life cycle cost (T=40y, dr=0) | LCC 2 |  | €
Life cycle cost (T=25y, dr=0.05) | LCC 4 |  | €
Life cycle cost (T=25y, dr=0) | LCC 5 |  | €
Life cycle cost (T=10y, r=0.05) | LCC 8 |  | €
Life cycle cost (T=10y, r=0) | LCC 7 |  | €