## 1-Goal and scope definition
Transmission link between solar plant and substation
Phase 1: Goal and scope definition
Goal | Product system | HTS cable system
| Intended application and reasons for study | Comparison with HTS cable system
| Brief description | Transmission link between solar plant and substation
| Intended audience | Tutorial HTS school COST ACTION Hi-scale
| Comissioners and assessors | L. Quéval & A. Musso
| Limitations of study | Do not trust the data !
Scope | System boundary | Cable system including transformer
| Benchmark system | 400 kV underground cable
| Plant size | 1.5 GW
| Functional unit | 750 MW
| System elements and technology maturity | TRL 9
| Performance indicators | Life cycle cost (LCC)
| Time horizon | 40 years
| Location | Saudi Arabia
| Operation continuity | 8 hours a day

## 2-Inventory analysis-HTS
Transmission link between solar plant and substation
Phase 2: Inventory analysis
HTS system MAIN FEATURES
Technical parameter | Symbol | HTS system | Units | Comment
Number of HTS cable systems running in parallel | n_cables | 2
Line length for each cable | L_line | 32000 | m |  | Technical model legend
Power delivered by each cable | P | 750000000 | W | Maximum Power for 1 cable = 750 MW |  | Cable design parameter set by user (eventually modifiable)
Voltage level rms of each cable | Vrms | 33000 | V | Phase-to-phase voltage (rms value) |  | Computed (not to be changed)
Load factor | cosφ | 0.95 |  |  |  | Material property set by the user (eventually modifiable)
Mean ambient temperature in the installation site | Ta | 303.15 | K | 30° C
Frequency | f | 50 | Hz |  | Economic model legend
Set by user (eventually modifiable)
HTS tapes
Technical parameter | Symbol | HTS system | Units | Comment
Tape width | w_HTS | 0.004 | m
Mean HTS temperature in the cable, for all phases (tentative) | T_HTS | 70.1 | K
Critical current of the tape at 77 K and s.f. | Ic_HTS_77K | 293.7 | A
Safety value of I_tape/Ic_HTS not to be passed | safety_HTS | 0.8 |  | 80%
N° of HTS layers in phase 1 | nl_1 | 2
N° of HTS layers in phase 2 | nl_2 | 1
N° of HTS layers in phase 3 | nl_3 | 1
Inner radius of HTS layer 1 - phase 1 | RHTS_1_1 | 0.0339 | m
Inner radius of HTS layer 2 - phase 1 | RHTS_2_1 | 0.0341 | m
Inner radius of HTS layer 1 - phase 2 | RHTS_1_2 | 0.048621 | m
Inner radius of HTS layer 1 - phase 3 | RHTS_1_3 | 0.062376 | m
Twist angle of HTS layer 1 - phase 1 | α1_1 | 11 | °
Twist angle of HTS layer 2 - phase 1 | α2_1 | 15 | °
Twist angle of HTS layer 1 - phase 2 | α1_2 | -13 | °
Twist angle of HTS layer 1 - phase 3 | α1_3 | -14 | °
n° of HTS tapes in layer 1 - phase 1 | Tapes_1_1 | 52 |  | Tapes_1_1 = round[2 * π * RHTS_1_1 * cos (α1_1) / w_HTS]
n° of HTS tapes in layer 2 - phase 1 | Tapes_2_1 | 52 |  | Tapes_2_1 = round[2 * π * RHTS_2_1 * cos (α2_1) / w_HTS]
n° of HTS tapes in layer 1 - phase 2 | Tapes_1_2 | 74 |  | Tapes_1_2 = round[2 * π * RHTS_1_2 * cos (α1_2) / w_HTS]
n° of HTS tapes in layer 1 - phase 3 | Tapes_1_3 | 95 |  | Tapes_1_3 = round[2 * π * RHTS_1_3 * cos (α1_3) / w_HTS]
Economic parameter | Symbol | HTS system | Units | Comment
CAPEX
HTS tape cost per unit of length | c_HTS | 30 | €/m
Copper
Technical parameter | Symbol | HTS system | Units | Comment
Inner radius of copper neutral layer | R_int_neutral | 0.075755 | m
Outer radius of copper neutral layer | R_ext_neutral | 0.077755 | m
Eddy current loss per unit of length and unit of current | q_eddy | 0.05 | mW/(kA*m)
Copper density | ρ_Cu | 8850 | kg/m3
Economic parameter | Symbol | HTS system | Units | Comment
CAPEX
Copper cost per unit of weight | c_Cu | 7 | €/kg
Insulation
Technical parameter | Symbol | HTS system | Units | Comment
Inner radius of insulating layer between phase 1 and phase 2 | R_int_ins_1 | 0.03425 | m
Outer radius of insulating layer between phase 1 and phase 2 | R_ext_ins_1 | 0.048621 | m
Inner radius of insulating layer between phase 2 and phase 3 | R_int_ins_2 | 0.048771 | m
Outer radius of insulating layer between phase 2 and phase 3 | R_ext_ins_2 | 0.062376 | m
Inner radius of insulating layer outside phase 3 | R_int_ins_3 | 0.062526 | m
Outer radius of insulating layer outside phase 3 | R_ext_ins_3 | 0.075755 | m
Loss tangent | tand_ins | 0.0006
Relative permettivity | ε_ins | 2.21
Insulation density | ρ_ins | 900 | kg/m3 | 0.9 ton/m3
Economic parameter | Symbol | HTS system | Units | Comment
CAPEX
Insulation cost per unit of weight | c_ins | 10 | €/kg
LN2 and cooling channels
Technical parameter | Symbol | HTS system | Units | Comment
Former radius | Rformer | 0.03 | m
Inner radius of the annular gap | R_int_annulus | 0.078555 | m
Outer radius of the annular gap | R_ext_annulus | 0.10635 | m
Roughness of the inner surface of the former | ε_former | 0.0014 | m
Roughness of the inner surface of the annular gap | ε_annulus | 0.0014 | m
Height difference between the two ends of each cable section | Δh | 1 | m
LN2 heat capacity | cp_LN2 | 2662 | J/kg*K
LN2 dynamic viscosity | 𝜇_LN2 | 2.508e-05 | Pa∙s
LN2 density | ρ_LN2 | 839 | kg/m3
kg on liter ratio for LN2 | kg_l_LN2 | 1.235 | kg/l
LN2 temperature at the beginning of each cable section | T_0 | 68 | K
Mean LN2 temperature in the annular gap (tentative) | T_annulus | 70.4 | K
Maximum temperature rise allowed for the LN2 in both ducts | ΔT_LN2_max | 10 | K
Maximum pressure drop allowed for the LN2 in both ducts | ΔP_LN2_max | 12 | bar
Annular gap thickness | t_annulus | 0.0278 | mm
LN2 mass flow rate | m_LN2 | 2.15 | kg/s
Economic parameter | Symbol | HTS system | Units | Comment
CAPEX
LN2 cost per liter | c_LN2 | 0.16 | €/l
Cryostat
Technical parameter | Symbol | HTS system | Units | Comment
Effective thermal conductivity of the cryostat | λ_cryo | 0.0004 | W/m K
Economic parameter | Symbol | HTS system | Units | Comment
CAPEX
Cryostat cost per unit of length | c_cryo | 220000 | €/km
Terminations
Technical parameter | Symbol | HTS system | Units | Comment
N° of terminations (both cable ends) | n_term | 6
Loss for each termination per unit of current | q_term | 45 | W/kA
Economic parameter | Symbol | HTS system | Units | Comment
CAPEX
Terminations costs | C_term | 400000 | €
Cooling stations
Technical parameter | Symbol | HTS system | Units | Comment
n° of intermediate cooling stations | nstat | 5
Crycoolers efficiency | η_cryo | 0.1 |  | 10%
Pumps efficiency | η_p | 0.7 |  | 70%
Economic parameter | Symbol | HTS system | Units | Comment
CAPEX
Fixed costs for each cooling station | c_cool_fixed | 500000 | €
Costs per unit of power of cryocoolers | c_cool_var | 25 | €/W
OPEX
Mark-up to consider possible heat peaks | 𝛽q | 1.1 |  | 10% of mark-up
Mark-up for the devices with no parametric cost function | 𝛽r | 1.1 |  | 10% of mark-up
Land
Technical parameter | Symbol | HTS system | Units | Comment
Radius from the cable where Bfield < 6 μT | R_field | 0.3 | m | Computed from magnetic field calculations
Economic parameter | Symbol | HTS system | Units | Comment
CAPEX
Land cost per unit of surface | c_land | 20 | €/m2
Cabling
Economic parameter | Symbol | HTS system | Units | Comment
CAPEX
Cabling cost per unit of length | c_cab | 1000000 | €/km | Cost for manufacturing the cable from its constituting elements
Vacuum system
Economic parameter | Symbol | HTS system | Units | Comment
CAPEX
Vacuum system costs per unit of length | c_vac | 52000 | €/km
Maintenance
Economic parameter | Symbol | HTS system | Units | Comment
OPEX
Maintenance costs per unit of length and per year | c_maint | 3000 | €/km/year
Dismantling
Economic parameter | Symbol | HTS system | Units | Comment
CAPEX
Dismantling costs per unit of length | c_dism | 20000 | €/km
Commissionining, Installation, Civil Eng., Regulation, Accessories
Economic parameter | Symbol | HTS system | Units | Comment
CAPEX
Other costs per unit of length | c_other | 800000 | €/km
Other Info
Economic parameter | Symbol | HTS system | Units | Comment
OPEX
Energy cost | c_en | 0.015 | €/kWh
Nb of full load hours per year | nhpy | 2920 | hours | 8 hours a day in a year
LCC
Time horizon | T | 40 | years | 40
Discount rate | r | 0.05 |  | 5%
Note on D12: Musso Andrea (RSE):

## 3.0-HTS Cable design
Transmission link between solar plant and substation
Phase 2.5: Compute cable design, losses and constraints
HTS system MAIN FEATURES |  |  |  |  | Constants
Technical parameter | Symbol | HTS system | Units | Comment | Technical parameter | Symbol | HTS system | Units
Line length | L_line | 32000 | m |  | Vacuum permeability | μ0 | 1.2566e-06 | H/m
Power delivered by each cable | P | 750000000 | W |  | Gravitational constant | g | 9.81 | m/s^2
Voltage level rms of each cable | Vrms | 33000 | V |  | Dielectric constant of vacuum | ε0 | 8.854e-12 | C^2/(N*m^2)
Frequency | f | 50 | Hz
load factor | cosφ | 0.95
Mean ambient temperature in the installation site | Ta | 303.15 | K
Rms value of the total current in each phase | Irms_phase | 13812.2074 | A | Irms_phase = P / (Vrms *√3 * cosφ)
Rms value of the current in HTS layer 1 - phase 1 | Irms_1_1 | 6906.1037 | A | Irms_1_1 = Irms_phase/nl_1
Rms value of the current in HTS layer 1 - phase 2 | Irms_1_2 | 6906.1037 | A | Irms_1_2 = Irms_phase/nl_1
Rms value of the current in HTS layer 1 - phase 3 | Irms_1_3 | 13812.2074 | A | Irms_1_3 = Irms_phase/nl_2
Rms value of the current in HTS layer 1 - phase 4 | Irms_1_3 | 13812.2074 | A | Irms_1_3 = Irms_phase/nl_3
Cable design in cascade |  |  |  |  | Insulation thickness parameters |  |  |  |  | Losses in a single cable system |  |  |  |  | Constraints calculation
Technical parameter | Symbol | HTS system | Units | Comment | Technical parameter | Symbol | HTS system | Units | Comment | Technical parameter | Symbol | HTS system | Units | Comment | Technical parameter | Symbol | HTS system | Units | Comment
Former radius | Rformer | 0.03 | m |  |  | k1_im | 1 |  |  | n° of intermediate cooling stations | nstat | 5 |  |  | Velocity of LN2 into the former | v_LN2_former | 0.90633 | m/s
Thickness of the former | t_f | 0.002 | m |  |  | k2_im | 1 |  |  | Distance between adjacent cooling statio | dstat | 5333.3333 | m | dstat = L_line / (nstat + 1) | Velocity of LN2 into the annular gap | v_LN2_annulus | 1.0554 | m/s
Thickness of the levelling layer between former and innermost HTS layer | t_lev | 0.0019 | m |  |  | k3_im | 1.2 |  |  | AC losses in HTS tapes |  |  |  |  | Reynolds number for LN2 in the former | Re_LN2_former | 1819155.3836
Inner radius of HTS layer 1 - phase 1 | RHTS_1_1 | 0.0339 | m | RHTS_1_1 = Rformer + t_f + t_lev |  | V_im | 750000 | V |  | Technical parameter | Symbol | HTS system | Units | Comment | Reynolds number for LN2 in the annular gap | Re_LN2_annulus | 1963117.3204
Thickness of HTS tapes | t_HTS | 0.00015 | m |  |  | E_im | 75000000 | V/m |  | n° of HTS tapes in layer 1 - phase 1 | Tapes_1_1 | 52 |  | Tapes_1_1 = round[2 * π * RHTS_1_1 * cos (α1_1) / w_HTS] | Friction factor for LN2 in the former | f_LN2_former | 0.0097635
Thickness of layer between HTS layers of the same phase | t_k | 5e-05 | m |  |  | k1_AC | 1.4 |  |  | n° of HTS tapes in layer 2 - phase 1 | Tapes_2_1 | 52 |  | Tapes_2_1 = round[2 * π * RHTS_2_1 * cos (α2_1) / w_HTS] | Friction factor for LN2 in the annular gap | f_LN2_annulus | 0.010063
Inner radius of HTS layer 2 - phase 1 | RHTS_2_1 | 0.0341 | m | RHTS_2_1 = RHTS_1_1 + t_HTS + t_k |  | k2_AC | 1 |  |  | n° of HTS tapes in layer 1 - phase 2 | Tapes_1_2 | 74 |  | Tapes_1_2 = round[2 * π * RHTS_1_2 * cos (α1_2) / w_HTS] | Temperature rise
Inner radius of insulating layer between phase 1 and phase 2 | R_int_ins_1 | 0.03425 | m | R_int_ins_1 = RHTS_2_1 + t_HTS |  | k3_AC | 1.2 |  |  | n° of HTS tapes in layer 1 - phase 3 | Tapes_1_3 | 95 |  | Tapes_1_3 = round[2 * π * RHTS_1_3 * cos (α1_3) / w_HTS] | Temperature rise for LN2 in the former | ΔT_LN2_former | 3.514 | K
Thickness of insulating layer between phase 1 and phase 2 | t_ins_1 | 0.014371 | m | from insulation parameters and line voltage |  | V_AC | 67360.9679 | V |  | Twist angle of HTS layer 1 - phase 1 | α1_1 | 11 | ° |  | Temperature rise for LN2 in the annular gap | ΔT_LN2_annulus | 4.618 | K
Outer radius of insulating layer between phase 1 and phase 2 | R_ext_ins_1 | 0.048621 | m | R_ext_ins_1 = R_int_ins_1 + t_ins_1 |  | E_AC | 52000000 | V/m |  | Twist angle of HTS layer 2 - phase 1 | α2_1 | 15 | ° |  | Maximum temperature for LN2 in the former | T_max_LN2_former | 71.514 | K
Inner radius of HTS layer 1 - phase 2 | RHTS_1_2 | 0.048621 | m | RHTS_1_2 = R_ext_ins_1 | [5 empty] | Twist angle of HTS layer 1 - phase 2 | α1_2 | -13 | ° |  | Maximum temperature for LN2 in the annular gap | T_max_LN2_annulus | 72.618 | K
Inner radius of insulating layer between phase 2 and phase 3 | R_int_ins_2 | 0.048771 | m | R_int_ins_2 = RHTS_1_2 + t_HTS | [5 empty] | Twist angle of HTS layer 1 - phase 3 | α1_3 | -14 | ° |  | Mean temperature for LN2 in the former | T_former | 69.757 | K
Thickness of insulating layer between phase 1 and phase 2 | t_ins_2 | 0.013605 | m | from insulation parameters and line voltage | [5 empty] | Critical current of HTS tapes at T_HTS (mean temperature) | Ic_HTS_T_HTS | 430.4937 | A |  | Mean temperature for LN2 in the annular gap | T_annulus | 70.309 | K
Outer radius of insulating layer between phase 1 and phase 2 | R_ext_ins_2 | 0.062376 | m | R_ext_ins_2 = R_int_ins_2 + t_ins_2 | [5 empty] | F_ratio of HTS tapes in layer 1 - phase 1 | F_1_1 | 0.43629 |  |  | Temperature of HTS tapes at left side of a cable segment | T_HTS_left | 69.757 | K
Inner radius of HTS layer 1 - phase 3 | RHTS_1_3 | 0.062376 | m | RHTS_1_3 = R_ext_ins_2 | [5 empty] | F_ratio of HTS tapes in layer 2 - phase 1 | F_2_1 | 0.43629 |  |  | Temperature of HTS tapes at right side of a cable segment | T_HTS_right | 70.309 | K
Inner radius of insulating layer outside phase 3 | R_int_ins_3 | 0.062526 | m | R_int_ins_3 = RHTS_1_3 + t_HTS | [5 empty] | F_ratio of HTS tapes in layer 1 - phase 2 | F_1_2 | 0.61317 |  |  | Mean HTS temperature in the cable, for all phases | T_HTS | 70.033 | K
Thickness of insulating layer outside phase 3 | t_ins_3 | 0.013229 | m | from insulation parameters and line voltage | [5 empty] | F_ratio of HTS tapes in layer 1 - phase 3 | F_1_3 | 0.47763 |  |  | Pressure drop
Outer radius of insulating layer outside phase 3 | R_ext_ins_3 | 0.075755 | m | R_ext_ins_3 = R_int_ins_3 + t_ins_3 | [5 empty] | ξ of HTS tapes in layer 1 - phase 1 | ξ_1_1 | 0.006552 |  |  | Pressure drop for LN2 in the former [Pa] | ΔP_LN2_former | 307287.1205 | Pa
Copper layer inner radius | R_int_neutral | 0.075755 | m | R_int_neutral = R_int_neutral | [5 empty] | ξ of HTS tapes in layer 2 - phase 1 | ξ_2_1 | 0.006552 |  |  | Pressure drop for LN2 in the annular gap [Pa] | ΔP_LN2_annulus | 459328.1351 | Pa
Thickness of copper neutral layer | t_n | 0.002 | m | [6 empty] | ξ of HTS tapes in layer 1 - phase 2 | ξ_1_2 | 0.028042
Outer radius of copper neutral layer | R_ext_neutral | 0.077755 | m | R_ext_neutral = R_int_neutral + t_n | [5 empty] | ξ of HTS tapes in layer 1 - phase 3 | ξ_1_3 | 0.0095781
Thickness of core fixture layer between netrual and annular gap | t_c | 0.0008 | m | [6 empty] | Losses of HTS tapes in layer 1 - phase 1 | Loss_AC_HTS_1_1 | 39667.88 | W
Inner radius of the annular gap | R_int_annulus | 0.078555 | m | R_int_annulus = R_ext_neutral + t_c | [5 empty] | Losses of HTS tapes in layer 2 - phase 1 | Loss_AC_HTS_2_1 | 39033.383 | W
Thickness of the annular gap | t_annulus | 0.0278 | m | [6 empty] | Losses of HTS tapes in layer 1 - phase 2 | Loss_AC_HTS_1_2 | 239820.0231 | W
Outer radius of the annular gap | R_ext_annulus | 0.10635 | m | R_ext_annulus = 'R_int_annulus + t_annulus | [5 empty] | Losses of HTS tapes in layer 1 - phase 3 | Loss_AC_HTS_1_3 | 104717.7415 | W
Inner radius of the cryostat | R_int_cryo | 0.10635 | m | R_int_cryo = R_ext_annulus | [5 empty] | Total AC losses in the HTS tapes of the whole cable | Loss_AC_HTS | 423239.0276 | W
Thickness of the cryostat wall | t_cryo | 0.0318 | m | [6 empty] | Insulation losses
Outer radius of the cryostat | R_ext_cryo | 0.13815 | m | R_ext_cryo = R_int_cryo | [5 empty] | Technical parameter | Symbol | HTS system | Units | Comment
[10 empty] | Capacitance of insulating layer between phase 1 and phase 2 | Capac_1 | 3.5091e-10 | F
[10 empty] | Capacitance of insulating layer between phase 2 and phase 3 | Capac_2 | 4.9968e-10 | F
[10 empty] | Capacitance of insulating layer outside phase 3 | Capac_3 | 6.4061e-10 | F
[10 empty] | Losses of insulating layer between phase 1 and phase 3 | Loss_ins_1 | 2304.9949 | W
[10 empty] | Losses of insulating layer between phase 2 and phase 4 | Loss_ins_2 | 3282.2323 | W
[10 empty] | Losses of insulating layer outside phase 4 | Loss_ins_3 | 4207.9454 | W
[10 empty] | Total losses in the 3 insulating layers | Loss_ins | 9795.1727 | W
Losses from cryostat
[10 empty] | Technical parameter | Symbol | HTS system | Units | Comment
[10 empty] | Total losses from cryostat in the whole cable | Loss_cryo | 71556.9467 | W
Losses due to eddy currents
[10 empty] | Technical parameter | Symbol | HTS system | Units | Comment
[10 empty] | Total losses due to eddy currents in the whole cable | Loss_eddy | 31253.4576 | W
Losses from the terminations
[10 empty] | Technical parameter | Symbol | HTS system | Units | Comment
[10 empty] | Total losses from the terminations | Loss_term | 5274.021 | W
Total losses in the whole cable
[10 empty] | Technical parameter | Symbol | HTS system | Units | Comment
[10 empty] | Total losses in the whole cable | Losses | 541118.6255 | W
Loss components to LN2 and single terminations
[10 empty] | Technical parameter | Symbol | HTS system | Units | Comment
[10 empty] | Heat input in the LN2 flowing in the former | Q_f | 38690.6382 | W
[10 empty] | Heat input in the LN2 flowing in the annular gap | Q_an | 50616.7959 | W
[10 empty] | Heat produced by the terminations in a single cable end | Q_cl | 2637.0105 | W
Note on D9: Musso Andrea (RSE):

## 3-Calculation of indicators
Transmission link between solar plant and substation
Phase 3: Calculation of indicators
Technical model for a single cable system
Variable | Symbol | HTS system | Units | Comment
MATERIALS for 1 cable system
HTS tape length for phase 1 | L_HTS_1 | 3417844.1446 | m | L_HTS_1 = (Tapes_1_1 + Tapes_2_1)* L_line / cos(α1_1)
HTS tape length for phase 2 | L_HTS_2 | 2430288.1273 | m | L_HTS_2 = Tapes_1_2 * L_line / cos(α1_2)
HTS tape length for phase 3 | L_HTS_3 | 3133065.4332 | m | L_HTS_3 = Tapes_1_3 * L_line / cos(α1_3)
Volume of the copper for the neutral layer | Vol_Cu | 30.865 | m3 | Vol_Cu = L_line * π * (R_ext_neutral^2 - Rint_neutral^2)
Volume of the insulation between phase 1 and 2 | Vol_ins_1 | 119.7244 | m3 | Vol_ins_1 = = L_line * π * (R_ext_ins_1^2 - Rint_ins_1^2)
Volume of the insulation between phase 2 and 3 | Vol_ins_2 | 152.0204 | m3 | Vol_ins_2 = L_line * π * (R_ext_ins_2^2 - Rint_ins_2^2)
Volume of the insulation outside phase 3 | Vol_ins_3 | 183.9012 | m3 | Vol_ins_3 = L_line * π * (R_ext_ins_3^2 - Rint_ins_3^2)
Volume of LN2 into the whole cable | Vol_LN2 | 607.2564 | m3 | Vol_LN2 = L_line * π * (R_ext_annulus^2 - Rint_annulus^2 + Rformer^2)
COOLING STATIONS for 1 cable system
Heat input in the LN2 flowing in the former | Q_f | 38.6906 | kW | From loss calculation
Heat input in the LN2 flowing in the annular gap | Q_an | 50.6168 | kW | From loss calculation
Heat produced by the terminations in a single cable end | Q_cl | 2.637 | kW | From loss calculation
Heat to be removed by each intermediate cooling station from LN2 | Q_interm | 89.3074 | kW | Q_interm = Q_f + Q_an
Heat to be removed by left-side cooling station from LN2 | Q_left | 53.2538 | kW | Q_left = Q_an + Q_cl
Heat to be removed by right-side cooling station from LN2 | Q_right | 41.3276 | kW | Q_right = Q_f + Q_cl
Pressure drop in the LN2 flowing in the former [Pa] | ΔP_LN2_former | 307287.1205 | Pa
Pressure drop in the LN2 flowing in the annular gap [Pa] | ΔP_LN2_annulus | 459328.1351 | Pa
Hydraulic power by each intermediate cooling station | Qp_interm | 1.9645 | kW | Qp_interm = m_LN2 * (ΔP_f + ΔP_an) / ρ_LN2
Hydraulic power by left-side cooling station | Qp_left | 1.1771 | kW | Qp_left = m_LN2 * (ΔP_an) / ρ_LN2
Hydraulic power by right-side cooling station | Qp_right | 0.78745 | kW | Qp_right = m_LN2 * (ΔP_f) / ρ_LN2
Electric power to supply each intermediate cooling station | Pel_interm | 3091.1363 | kW | Pel_interm = Q_interm * (Ta - T_0)/(η_cryo * T_0) + (Qp_interm / η_pump)
Electric power to supply left-side cooling station | Pel_left | 1843.2451 | kW | Pel_left = Q_left * (Ta - T_0)/(η_cryo * T_0) + (Qp_left / η_pump)
Electric power to supply right-side cooling station | Pel_right | 1430.2715 | kW | Pel_right = Q_right * (Ta - T_0)/(η_cryo * T_0) + (Qp_right / η_pump)
VERIFY CONSTRAINTS AND CHECK QUALITY OF TENTATIVE TEMP.S
Temperature rise in the LN2 flowing in the former | ΔT_LN2_former | 3.514 | K
Temperature rise in the LN2 flowing in the annular gap | ΔT_LN2_annulus | 4.618 | K
Maximum temperature rise allowed for the LN2 in both ducts | ΔT_LN2_max | 10 | K
Pressure drop in the LN2 flowing in the annular gap [bar] | ΔP_LN2_annulus | 3.0729 | bar
Pressure drop in the LN2 flowing in the annular gap [bar] | ΔP_LN2_annulus | 4.5933 | bar
Maximum pressure drop allowed for the LN2 in both ducts | ΔP_LN2_max | 12 | bar
Mean LN2 temperature in the annular gap (TENTATIVE) | T_annulus | 70.4 | K
Mean LN2 temperature in the annular gap (COMPUTED) | T_annulus | 70.309 | K
Mean HTS temperature in the cable (TENTATIVE) | T_HTS | 70.1 | K
Mean HTS temperature in the cable (COMPUTED) | T_HTS | 70.033 | K
Critical current of HTS tapes at maximum temperature | Ic_HTS_T_HTS_max | 426.4797 | A
Ratio between Imax in HTS tapes and their Ic in layer 1 - phase 1 | Imax_1_1/Ic_HTS_T_HTS_max | 0.4404 |  | Imax_1_1/Ic_HTS_T_HTS_max = (√2 * Irms_1_1 / Tapes_1_1) / Ic_HTS_T_HTS_max
Ratio between Imax in HTS tapes and their Ic in layer 2 - phase 1 | Imax_2_1/Ic_HTS_T_HTS_max | 0.4404 |  | Imax_2_1/Ic_HTS_T_HTS_max = (√2 * Irms_2_1 / Tapes_2_1) / Ic_HTS_T_HTS_max
Ratio between Imax in HTS tapes and their Ic in layer 1 - phase 2 | Imax_1_2/Ic_HTS_T_HTS_max | 0.61894 |  | Imax_1_2/Ic_HTS_T_HTS_max = (√2 * Irms_1_2 / Tapes_1_2) / Ic_HTS_T_HTS_max
Ratio between Imax in HTS tapes and their Ic in layer 1 - phase 3 | Imax_1_3/Ic_HTS_T_HTS_max | 0.48212 |  | Imax_1_3/Ic_HTS_T_HTS_max = (√2 * Irms_1_3 / Tapes_1_3) / Ic_HTS_T_HTS_max
Safety value of I_tape/Ic_HTS not to be passed | safety_HTS | 0.8
Economic model for all cables running in parallel
Variable | Symbol | HTS system | Units | Comment
MATERIALS
HTS tape CAPEX | C_HTS | 538.8719 | M€ | C_HTS = n_cables * c_HTS * (L_HTS_1 + L_HTS_2 + L_HTS_3)
Copper CAPEX | C_Cu | 3.8242 | M€ | C_Cu = n_cables * c_Cu * ρ_Cu * Vol_Cu
Insulation CAPEX | C_ins | 8.2016 | M€ | C_ins = n_cables * c_ins * ρ_ins * (Vol_ins_1 + Vol_ins_2 + Vol_ins_3)
LN2 CAPEX | C_LN2 | 0.00023999 | M€ | C_LN2 = n_cables * c_LN2 * kg_l_LN2 * Vol_LN2
Cryostat CAPEX | C_cryo | 14.08 | M€ | C_cryo = n_cables * c_cryo * L_line [be careful if you are multiplying €/km or €/m by the cable lenght in km or meters]
Terminations CAPEX | C_term | 0.8 | M€ | n_cables * C_term
COOLING STATIONS
Cooling stations CAPEX | C_cool | 7.0327 | M€ | C_cool = n_cables * nstat * [c_cool_fixed + (c_cool_var * Q_interm * βq * βr)] + n_cables * [c_cool_fixed + (c_cool_var * Q_left * βq * βr)] + n_cables *[c_cool_fixed + (c_cool_var * Q_right * βq * βr)]
Yearly cooling stations OPEX | O_cool_t | see table | M€/year | O_cool_t = n_cables * c_en * nhpy * [(nstat * Pel_interm) + Pel_left + Pel_right)]
Total cooling stations OPEX discounted at t=0 | O_cool | 15.7581 | M€ | OPEX_cool = ΣOPEX_cool_t/ (1+r)^t
LAND
Land CAPEX | C_land | 0.768 | M€ | C_land = n_cables * c_land * L_line * (2 * R_field)
CABLING
Cabling CAPEX | C_cab | 64 | M€ | C_cab = n_cables * c_cab * L_line
VACUUM SYSTEM
Vacuum system CAPEX | C_vac | 3.328 | M€ | C_vac = n_cables * c_vac * L_line
DISMANTLING
Dismantling CAPEX | C_dism | 0.18182 | M€ | C_dism = n_cables * c_dism * L_line / [(1+r)^T]
OTHER COSTS
Other costs CAPEX | C_other | 51.2 | M€ | C_other = n_cables * c_other * L_line
MAINTENANCE
Yearly maintenance OPEX | O_maint_t | see table | M€/year | OPEX_maint_t = n_cables * c_maint * L_line
Total maintenance OPEX discounted at t=0 | O_maint | 3.2945 | M€ | OPEX_maint = ΣOPEX_maint_t/(1+r)^t
TOTAL
Capital expenditure (to be discounted) | CAPEX_t | 692.2885 | M€ | CAPEX_t = C_HTS + C_Cu + C_ins + C_LN2 + C_cryo + C_term + C_cool + C_land + C_cab + C_vac + C_dism + C_other
Capital expenditure discounted at t=0 | CAPEX | 659.3223 | M€ | CAPEX = ΣCAPEX_t/(1+r)^t
Yearly operational expenditure (to be discounted) | OPEX_t | see table | M€/year | OPEX_t = O_cool_t + O_maint_t
Total operational expenditure discounted at t=0 | OPEX | 19.0526 | M€ | ΣOPEX_t/(1+r)^t
Life cycle cost | LCC | 678.3749 | M€ | CAPEX + OPEX
[6 empty] | NOT Discounted cost |  |  |  | Discounted cost
[5 empty] | Year | O_cool_t | O_maint_t | OPEX_t | CAPEX_t | O_cool_t | O_maint_t | OPEX_t | CAPEX | Units
[5 empty] | 1 | 1.6407 | 0.192 | 1.8327 | 692.2885 | 1.5626 | 0.18286 | 1.7454 | 659.3223 | M€
[5 empty] | 2 | 1.4881 | 0.192 | 1.6801 | 0 | 1.3498 | 0.17415 | 1.5239 | 0 | M€
[5 empty] | 3 | 1.4173 | 0.192 | 1.6093 | 0 | 1.2243 | 0.16586 | 1.3902 | 0 | M€
[5 empty] | 4 | 1.3498 | 0.192 | 1.5418 | 0 | 1.1105 | 0.15796 | 1.2684 | 0 | M€
[5 empty] | 5 | 1.2855 | 0.192 | 1.4775 | 0 | 1.0072 | 0.15044 | 1.1577 | 0 | M€
[5 empty] | 6 | 1.2243 | 0.192 | 1.4163 | 0 | 0.91359 | 0.14327 | 1.0569 | 0 | M€
[5 empty] | 7 | 1.166 | 0.192 | 1.358 | 0 | 0.82865 | 0.13645 | 0.9651 | 0 | M€
[5 empty] | 8 | 1.1105 | 0.192 | 1.3025 | 0 | 0.75161 | 0.12995 | 0.88157 | 0 | M€
[5 empty] | 9 | 1.0576 | 0.192 | 1.2496 | 0 | 0.68174 | 0.12376 | 0.8055 | 0 | M€
[5 empty] | 10 | 1.0072 | 0.192 | 1.1992 | 0 | 0.61835 | 0.11787 | 0.73623 | 0 | M€
[5 empty] | 11 | 0.95927 | 0.192 | 1.1513 | 0 | 0.56087 | 0.11226 | 0.67312 | 0 | M€
[5 empty] | 12 | 0.91359 | 0.192 | 1.1056 | 0 | 0.50872 | 0.10691 | 0.61563 | 0 | M€
[5 empty] | 13 | 0.87009 | 0.192 | 1.0621 | 0 | 0.46143 | 0.10182 | 0.56325 | 0 | M€
[5 empty] | 14 | 0.82865 | 0.192 | 1.0207 | 0 | 0.41853 | 0.096973 | 0.5155 | 0 | M€
[5 empty] | 15 | 0.78919 | 0.192 | 0.98119 | 0 | 0.37962 | 0.092355 | 0.47197 | 0 | M€
[5 empty] | 16 | 0.75161 | 0.192 | 0.94361 | 0 | 0.34432 | 0.087957 | 0.43228 | 0 | M€
[5 empty] | 17 | 0.71582 | 0.192 | 0.90782 | 0 | 0.31231 | 0.083769 | 0.39608 | 0 | M€
[5 empty] | 18 | 0.68174 | 0.192 | 0.87374 | 0 | 0.28328 | 0.07978 | 0.36306 | 0 | M€
[5 empty] | 19 | 0.64927 | 0.192 | 0.84127 | 0 | 0.25694 | 0.075981 | 0.33292 | 0 | M€
[5 empty] | 20 | 0.61835 | 0.192 | 0.81035 | 0 | 0.23305 | 0.072363 | 0.30541 | 0 | M€
[5 empty] | 21 | 0.58891 | 0.192 | 0.78091 | 0 | 0.21138 | 0.068917 | 0.2803 | 0 | M€
[5 empty] | 22 | 0.56087 | 0.192 | 0.75287 | 0 | 0.19173 | 0.065635 | 0.25737 | 0 | M€
[5 empty] | 23 | 0.53416 | 0.192 | 0.72616 | 0 | 0.17391 | 0.06251 | 0.23642 | 0 | M€
[5 empty] | 24 | 0.50872 | 0.192 | 0.70072 | 0 | 0.15774 | 0.059533 | 0.21727 | 0 | M€
[5 empty] | 25 | 0.4845 | 0.192 | 0.6765 | 0 | 0.14307 | 0.056698 | 0.19977 | 0 | M€
[5 empty] | 26 | 0.46143 | 0.192 | 0.65343 | 0 | 0.12977 | 0.053998 | 0.18377 | 0 | M€
[5 empty] | 27 | 0.43945 | 0.192 | 0.63145 | 0 | 0.11771 | 0.051427 | 0.16913 | 0 | M€
[5 empty] | 28 | 0.41853 | 0.192 | 0.61053 | 0 | 0.10676 | 0.048978 | 0.15574 | 0 | M€
[5 empty] | 29 | 0.3986 | 0.192 | 0.5906 | 0 | 0.096838 | 0.046646 | 0.14348 | 0 | M€
[5 empty] | 30 | 0.37962 | 0.192 | 0.57162 | 0 | 0.087835 | 0.044424 | 0.13226 | 0 | M€
[5 empty] | 31 | 0.36154 | 0.192 | 0.55354 | 0 | 0.079669 | 0.042309 | 0.12198 | 0 | M€
[5 empty] | 32 | 0.34432 | 0.192 | 0.53632 | 0 | 0.072262 | 0.040294 | 0.11256 | 0 | M€
[5 empty] | 33 | 0.32793 | 0.192 | 0.51993 | 0 | 0.065543 | 0.038376 | 0.10392 | 0 | M€
[5 empty] | 34 | 0.31231 | 0.192 | 0.50431 | 0 | 0.05945 | 0.036548 | 0.095998 | 0 | M€
[5 empty] | 35 | 0.29744 | 0.192 | 0.48944 | 0 | 0.053923 | 0.034808 | 0.088731 | 0 | M€
[5 empty] | 36 | 0.28328 | 0.192 | 0.47528 | 0 | 0.04891 | 0.03315 | 0.08206 | 0 | M€
[5 empty] | 37 | 0.26979 | 0.192 | 0.46179 | 0 | 0.044362 | 0.031572 | 0.075934 | 0 | M€
[5 empty] | 38 | 0.25694 | 0.192 | 0.44894 | 0 | 0.040238 | 0.030068 | 0.070306 | 0 | M€
[5 empty] | 39 | 0.2447 | 0.192 | 0.4367 | 0 | 0.036497 | 0.028636 | 0.065133 | 0 | M€
[5 empty] | 40 | 0.23305 | 0.192 | 0.42505 | 0 | 0.033104 | 0.027273 | 0.060377 | 0 | M€
[6 empty] | O_cool | O_maint | OPEX | CAPEX | O_cool | O_maint | OPEX | CAPEX
[5 empty] | SUM FOR 40 YEARS | 28.2307 | 7.68 | 35.9107 | 692.2885 | 15.7581 | 3.2945 | 19.0526 | 659.3223 | M€

## 4-Interpretation
Transmission link between solar plant and substation
Phase 4: Interpretation
Sensitivity analysis
Case | Conventional cable |  |  | HTS cable |  |  | Units
| LCC | CAPEX_0 | OPEX_0 | LCC | CAPEX_0 | OPEX_0
T = 40 y ; r = 0.05 ; c_en = 0.015 €/kWh ; nhpy = 8h/day ; c_HTS = 30 €/m ; c_land = 20 €/m2 ; Ic_HTS_77K = 293.7 A (REFERENCE) | [6 empty] | M€
T = 40 y ; r = 0.0 | [6 empty] | M€
T = 25 y ; r = 0.05 | [6 empty] | M€
c_en = 0.05 €/kWh | [6 empty] | M€
nhpy = 24h/day | [6 empty] | M€
c_HTS = 10 €/m | [6 empty] | M€
c_land = 120 €/m2 (and also Bfield < 0.5 μT --> R_field has to be increased) | [6 empty] | M€
Ic_HTS_77K = 250 A | [6 empty] | M€
w_HTS = 12 mm (and then multiply by 3 also the critical current and the cost, accordingly) | [6 empty] | M€